## Sheet1
IN ACCORDANCE TO THE 2022 CALIFORNIA FIRE CODE CHAPTER 10 SECTION 1032.10
1032.10 REQUIRED EMERGENCY LIGHTING SYSTEMS SHALL BE TESTED IN ACCORDANCE 1032.10-1032.10.2
1032.10.1 ACTIVATION TESTING OF REQUIRED EMERGENCY LIGHTING SYSTEMS SHALL BE PERMITTED TO BE CONDUCTED AS FOLLOWS:
1032.10.1 FUNCTIONAL TESTING SHALL BE CONDUCTED AT 30-DAY INTERVALS FOR NOT LESS THAN 30 SECONDS.
1032.10.2 POWER TEST FUNCTIONAL TESTING SHALL BE CONDUCTED ANNUALLY FOR NOTE LESS THAN 1 ½ HOURS IF THE EMERGENCY LIGHTING SYSTEM IS BATTERY POWERED.
THE EMERGENCY LIGHTING EQUIPMENT SHALL BE FULLY OPERATIONAL FOR THE DURATION OF THE TEST REQUIRED ABOVE.
109.3 WRITTEN RECORDS OF VISUAL INSPECTIONS AND TESTS SHALL BE KEPT BY THE OWNER FOR THE INSPECTION BY THE AUTHORITY HAVING JURISDICATION.
LOCATION | DATE | EXIT | EL | MAKE | MODEL | COLOR | BATTERY | 30 SECOND | 1 ½ HOUR TEST | PASS/FAIL | REPAIR | REPLACE | INTITAL | PO REPAIR
ADMIN | 2013-04-05 | X |  | DUALLITE | LX | RED | 1.2V 1.1AH | X |  | PASS |  |  | JMM
CAFTERIA | 2013-04-05 |  | X | LED UNIT | 120V | WHITE | AA Nicad |  | x | PASS |  |  | JMM
ROOM 100 | 2013-04-05 | X |  | DUALLITE | LX | RED | 1.2V 1.1AH |  | X | FAIL |  | X |  | 100345
LOCATION | DATE | EXIT | EL | MAKE | MODEL | COLOR | BATTERY | 30 SECOND | 1 ½ HOUR TEST | PASS/FAIL | REPAIR | REPLACE | INTITAL | PO REPAIR
LOCATION | DATE | EXIT | EL | MAKE | MODEL | COLOR | BATTERY | 30 SECOND | 1 ½ HOUR TEST | PASS/FAIL | REPAIR | REPLACE | INTITAL | PO REPAIR
EXAMPLE